## Current
Current Calibration - Read DAQ in each Current channel at 120.0V supply (L1) under different loads
Current Calibration
(constant current was 0.008A - subtracted from active loads)
| Current (A) | ChA (ADC Value) | ChB (ADC Value)
No Load | 0 | 8.87 | 27.23
Lights | 0.333 | 188332 | 35725
Lights+Heater | 1.955 | 1096320 | 206359

## Voltage
Voltage Calibration - Read DAQ in each multiplexer state with Different Supply Voltages
Forward Polarity (Normal Polarity)
|  | State A | State B
Measured Voltage | Measured Neutral Voltage | DAC_A | DAC_B
120.53 | 0.0597 | 1409447 | 3266145
90.45 | 0.0613 | 949988 | 2437335
128.62 | 0.0603 | 1539663 | 3491703
80.39 | 0.0572 | 817043 | 2157616
Reverse Polarity - Neutral and Line reversed
|  | State A | State B
Measured Volt | Measured Neutral Volt | DAC_A | DAC_B
120.51 | 0.0581 | 3262058 | 1435104
135.36 | 0.0579 | 3686127 | 1623925
78.92 | 0.0591 | 2124861 | 775733

## Power Factor
Power Factor Calibration - Read Power supply parameters under different loads at 120.0V supply(a fan motor and/or transformer used to provide reactive load)
Power Supply Values |  |  |  | non-calibrated PF Values
Current | Power | Power Factor | Current Factor | DAC_A | DAC_B
0.34 | 40.9 | 0.99 | 1.76 | 32250 | 32764 | lights
0.85 | 82.1 | 0.8 | 1.47 | 22441 | 26313 | fan high
0.64 | 63.2 | 0.827 | 1.58 | 23642 | 27073 | Fan Low +lights
0.705 | 65.2 | 0.763 | 1.56 | 21177 | 25066 | fan low + transformer
0.125 | 2.8 | 0.21 | 2.41 | 2076 | 7037 | transformer

## Calibration Checker
Scenario | Measured Value | ChA (ADC Value) | ChB (ADC Value)
No Load | 0 | 8.87 | 27.23
Lights | 0.333 | 188332 | 35725
Lights+Heater | 1.955 | 1096320 | 206359
Forward
Backwards Regression
(calibration M and B values from here)
| Backwards Regression |  | CHA - Gain | CHA - Offset | CHB - Gain | CHB - Offset
|  |  | 1.7842e-06 | -0.0013811 | 9.4847e-06 | -0.0027855